Temperature and Humidity Design Guidance

Hall B – CLAS12

Dave Kashy and Saptarshi Mandal

Jefferson Lab

February 2009.

Hall B has a long history of operation and much data on the temperature and humidity within the Hall. Studying this historical data and including likely calibration errors in the humidity sensors we determine the most likely conditions that the detectors will be exposed to over long periods.

Of highest concern is the temperature. There seems to be a direct correlation between wire breakage in our drift chambers and temperature excursions in the Hall.  The data is logged and if the temperatures get out of the normal range then alarms go off and our on call paging system alerts Hall B personnel to take actions to prevent the temperature excursions from getting too large.

From the temperature history of the last 10 years, it can be observed that the temperature at the floor level is approximately 700F. The history is shown in Fig. 1. A peak temperature of 790F was observed in January 2000 (shown in Fig. 2). During this peak, the temperature was above 750F for a period of approximately 12 hours. A low temperature of 630F was observed in December 2003 – January 2004. During this period, the temperature was below the 650F mark for 10 days. The temperature on Level 1 space frame is approximately 730F. During October 2003 two temperature spikes were observed at 840F and 800F. These spikes were only a couple of hours in duration. Temperature on Level 2 space frame is around the 740F mark with a peak around 800F. A low temperature of 660F was observed in December 2005 – January 2006.

The humidity at the floor level and on Level 2 space frame is around 55% in the summer months and around 35% in the winter months (shown in Fig.3). On Level 1 space frame it is around 60% in the summer and around 40% in the winter.

Based on the temperature and humidity history of the hall over the last 10 years, the ambient temperature of Hall B is 720F and humidity is 45%. A temperature change of +/- 100F would be a good estimate in designing for thermal expansion/contraction.

Fig.1 Temperature history at the Floor Level

Fig.2 Peak temperature at Floor Level

Fig.3 Humidity at Floor Level